## Slide 2: koelcursus
Steven Lecompte
DEPARTMENT OF electromechanical, systems and metal engineering
research group sustainable thermo-fluid Energy systems

## Slide 3: Basics

## Slide 4: Basics of refrigeration
Market overview
Thermodynamics
Applications and refrigeration systems
Heat driven cooling
Auxillary components
C02 installations
Compressors

## Slide 5: Refrigeration and its impact
Residentieel AC
Bron: EIU analyse
Chart: 
| Koeling | Industrie | Residentieel | Tertair | Landbouw | Transport | Andere
 | 17.2 | 37.6 | 20.5 | 17.1 | 2.6 | 1.6 | 3.4
Bron: IIR
Yearly growth (2018-2030)
%
Industriële koeling
Industriële koeling
Tertair AC
Industriële AC
Tertair koeling
Transport AC
Totaal
Residentiëlekoeling
Residentiële
AC
Share electricity use
Refrigeration
Industry
Residential
Tertiary
Agriculture
Transport
Other

## Slide 6: context
Challenges:
  Integration of renewable energy
  Climate and environment (ODP & GWP)
  Energy efficiency

## Slide 7: Vapour compression chiller
Heat absorption from cold body
Heat rejection to hot body
Not spontaneous, need work
    Clausius theorem (2nd law of thermodynamics)

## Slide 8: In practice: heat absorption (cold side)
Liquid refrigerant at low temperature
Heat transfer from cold body to refrigerant
Evaporation of refrigerant: at low pressure

## Slide 9: In practice: why evaporation
Latent heat: evaporation
Sensible heat: ΔT = 20 °C
  Large enthalpy difference between liquid and vapour
  Large heat absorption per unit of mass
  Large cooling capacity for low mass flow rate

## Slide 10: In practice: heat rejection (hot side)
Vapour refrigerant at higher temperature
Heat transfer from refrigerant to hot body
Condensation of refrigerant: at high pressure

## Slide 11: In practice: condensation
  Refrigerant at high temperature
  Condensaten of refrigerant: heat rejection to hot body
20° C, 5 bar
60° C, 17 bar

## Slide 12: Vapour compression chiller
Low pressure to high pressure transition with compressor
Transition from high pressure to low pressure with expansion valve

## Slide 13: Vapour compression chiller: nomenclature
Discharge line (persleiding)
Suction line (zuigleiding)
Liquid line (vloeistofleiding)

## Slide 14: PH diagram of vapour compression chiller (or heat pump)

## Slide 15: The ideal refrigeration cycle, P-h and t-S diagrams
No pressure drop over the heat exchangers
Saturated vapour at exit of the evaporator
Saturated liquid at exit of the condenser
Isentropic compressor

## Slide 16: Effect of subcooling in the condenser
Outlet of condenser is not perfectly saturated
Desuperheating
Condensation
Subcooling
Subcooling
But also: Asubcooling
Secondary medium
Capacity
pcondensation
COP

## Slide 17: Effect of superheating in the evaporator
Outlet of evaporator not perfectly saturated
Evaporation
Superheating
Secondary medium
Superheating
But also: Asuperheating
Capacity
(ρ )
pevaporation
COP

## Slide 18: Superheating affects compressor
Small superheating
  Risk of liquid droplets entering the compressor
    Pressure shock in compressor
    Foaming in oil sump
    Lubrication issues
Large superheating
  Limited discharge temperature
  Reduces COP
Superheating typically around 5°C

## Slide 19: Regulate superheating: expansion valves
At the inlet of the evaporator
Pressure reduction
Control superheat
  By regulating refrigerant flow rate evaporator
Different types
  Capillary
  Thermostatic
  Electronic

## Slide 20: Thermostatic expansion valve
Sensing bulbe: closed volume two phase refrigerant in contact with outlet evaporator
Pressure in sensing bulbe rises with temperature.

## Slide 21: Thermostatic valve characteristic
Valve opening depends on superheating
  When superhreating rises, valve opens
    Mass flow rate refrigrant increases
  When superhreating drops, valve closes
    Mass flow rate refrigerant drops
On average constant superheating
Oversized valve
Instable operation
Lag input sensing bulb
Sizing!

## Slide 22: Two stage compression and intercooling
Optimum intercooling pressure

## Slide 23: Two stage compression and intercooling

## Slide 24: Different temperature levels

## Slide 25: Reverse brayton
Qin
Qout
Wnet=Qout-Qin

## Slide 26: Heat driven heat pumps
Absorption
  Type I
  Type II
Adsorption
Ejector

## Slide 27: Absorption heat pump Overview
COP = 2
COP = 1/2
COP = 1/4
COP = 1.5
COP = 4
COP = 3
Type I
Type II

## Slide 28: TYPE I

## Slide 29: TYPE I & II
TYPE I
TYPE II

## Slide 30: Absorption heat pump Type I
Heating capacity | 1.000-70.000 kW
Driving heat source | Hot water 80-180 °C Steam 1-8 bar Flue gas 250-520 °C Direct fired with oil or gas
Heat source in | 15-60 °C process water
Using side out | 70-100 °C hot water
Ambient temperature | > 5°C, < 40°C
Capacity control | 100-20%
Load conditions | Stable base load
COPheating (Qg/Qc) | 1.65-1.8
Electrical power input | Qth << 5%

## Slide 31: Absorption heat pump Type II
Heating capacity | 1.000-70.000 kW
Heat source in | Hot water > 60 °C Exhaust steam > 90 °C
Using side out | 100-170 °C hot water
Cooling water out | < 40°C
Ambient temperature | > 5°C, <40 °C
Capacity control | 100-20%
Load conditions | Stable base load
COPheating (Qg/Qc) | 0.44-0.48
Electrical power input | Qth << 5%

## Slide 32: Absorption heat pumps market
Mainly Type I, 30 kWth to several MW
COP ~ 1.5-1.7
Temperature lift heat sink: 5°C to 40 °C
Heat sink outlet temperatures: 45°C to 95 °C
Manufacturers/suppliers:
  Robur
  Fulton
  Thermax
  Moretek Systems Inc
  Shuanglian
  Hitachi
  Yazaki
  Broad USA
  Colibri

## Slide 33: Thermally driven systems
Absorptioncooling: working fluid mixtures
Notes: R134a met amide en ether

## Slide 34: Adsorption cooling

## Slide 35: Ejector
Low COP
No moving parts, simple concept

## Slide 36: Free cooling

## Slide 37: Auxiliary components

## Slide 38: Auxiliary components: accumulator

## Slide 39: Auxiliary components: filter dryer

## Slide 40: Auxiliary components: oil separator

## Slide 41: Auxiliary components: liquid reciever

## Slide 42: Pump down operation

## Slide 43: Heat exchangers
Shell and tube
For heat transfer with liquid
Refrigerant in shell

## Slide 44: Heat exchangers
Fin and tube:
  Heat transfer with gas
Plates:
  Heat exchange with liquid
Tubes (refrigerant)
  Fins (air)

## Slide 45: Fin and tube heat exchangers
Different circuits in parallel (reduce pressure loss)
  Distributor
  In each circuit the same amount of working fluid

## Slide 46: Practical implementation: compressors
Volumetric compressors
  Piston compressor: 50 W - 110 kW
  Scroll compressor: 3 kW - 30 kW
  Screw compressor: 350 kW - 3500 kW
Turbo compressors
  Centrifugal compressor: > 200 kW, for large systems.

## Slide 47: Safe operation of compressors
Superheating shouldn’t be too high
  Otherwise refrigerant temperature too high
    Damage to electrical engine due to insufficient cooling
    Chemical reaction of refrigerant at higher temperatures
    Viscosity lubricating oil becomes too low
Superheating shouldn’t be too low
  Liquid refrigerant droplets mix with lubricating oil
  Friction evaporates the refrigerant and pushes lubricating oil away
  Large amounts of liquid can completely fill the swept volume, blocking the compressor
Correct choice of expansion valves guarantees correct operation

## Slide 48: Piston compressors operation
Clearance volume: cylinder never completely empty
Volume flow rate is smaller than swept volume x rotational speed

## Slide 49: Scroll compressor
Typical hermetic, 3 kW - 30 kW
Fixed spiral and eccentric movement
No dead volume

## Slide 50: Twin screw compressor
Semi-hermetic or open
No clearance volume

## Slide 51: Turbocompressor
Energy transfer between rotor and fluid (flow)
Volumetric flow rate heavily depended on pressure ratio
Typically semi-hermetic or open, large powers

## Slide 52: Compressor: Thermodynamic viewpoint
Actual compressors always give a periodic flow
  Piston compressor: stroke frequency
  Turbocharger: frequency with which blade passes
Average value over an appropriate period is constant!
  Both flow rate and discharge state
  So steady state analysis is possible
Three degrees of freedom per compressor for given pressures
  Mass flow
  Work (= electrical work)
  Heat transfer to the environment
Doesn't matter what type of compressor it is for the rest of the cycle!

## Slide 53: Three performance metrics for a compressor
For known suction temperature, suction pressure and discharge pressure:
Work expressed as isentropic efficiency:
Mass flow rate expressed as:
  Volumetric efficiency (filling factor)
  Not for turbocompressors
Heat loss expressed as loss coefficient:

## Slide 54: off-design operation
Notes: Sustainable solution for heat provision
Extract heat from a cold body
Reject heat to a hot body
Not spontaneous, needs work
Clausius statement
(2nd law of thermodynamics)

## Slide 55: Influence of temperature on COP
What if T condenser ?
What if T evaporator ?
(other boundary conditions identical)
Same trend as Carnot COP!

## Slide 56: Influence of temperature on Capacity
Assume reciprocating compressor
hermetic
semi-hermetic
open
High pressure ratios
Easy maintenance
Relatively cheap
Low capacity (RPM low)
Vibration prone

## Slide 57: Influence on mass flow rate
Volumetric efficiency:
Re-expansion loss:
p
V
Vc
Vr
Vint
Leakage loss
volumetric efficiency (%)
pressure ratio (pout/pin)

## Slide 58: Influence of temperature on capacity
What if T condenser ?
What if T evaporator ?

## Slide 59: Steven Lecompte DEPARTMENT OF electromechanical, systems and metal engineering E steven.lecompte@ugent.be T +32 9 264 33 55 M +32 470 04 55 24 www.ugent.be
Ghent University @ugent Ghent University