## Slide 1
25 September 2026
1 October 2026
Energik: Industriële warmtepompen

## Slide 2
Koen Demerie & Thomas De Cuyper
Equans Belux - Industry North
2-stage NH3 Heat Pump
25 September 2026
Version 1.1
Notes: imachs: Integrated maintenance automation cooling & hvac solutions

## Slide 3
01
02
03
AGFA Gevaert: customer information
Problem statement
Solution & technical details
Agenda

## Slide 4
01
Agfa Gevaert

## Slide 5
Notes: Printing: developments of inks,
H2: development of zircon membranes for elektrolysis
Medical: emulsions for medical imaging
Resulting a state-of-the-art chemical plants with 70 reactors, filters and drying equipment

## Slide 6
02
Problem statement

## Slide 7
Complex and high utility demand

## Slide 8
Complex and high utility demand
LOW TEMPERATURE
10/4°C circuit
HVAC buildings cooling
Process cooling
  Reactor jackets
  Adsorption dryers
MEDIUM TEMPERATURE
30/55°C circuit
HVAC buildings heating
(process)
HIGH TEMPERATURE
70/90/110°C circuit
Process heating
  Reactors
  Dryers
water cooled chillers
CHP/chillers
CHP/boilers
CTW
30/25°C circuit
Condensor cooling
Cooling towers

## Slide 9
Problem statement
Thermodynamic integration (coupling of the T-levels)
    Lots of waste heat on the MT
        Condensation heat of chillers
        MT circuit in summer!
Electrification
CHP no more certificates
Some of the water cooled chillers are EOL
Phasing out freon gases
Gas dependency

## Slide 10
03
Technical solution
Two-stage ammonia hybrid cooling & heat pump

## Slide 11
Title comes here
Installation to improve overall efficiency and flexibility by intergrating different temperature flows on a given footprint, no limitation regarding capacities

## Slide 12
Solution: 2-stage NH3 hybrid heat pump
HD C

## Slide 13
Solution: 2-stage NH3 hybrid heat pump
Concept design
2-stage NH3 heat pump
  LD CU (screw compressors)
  HD CU (piston compressors)
Open intercooler design
  Thermosiphon condensor
  Thermosiphon evaporator
2x subcooler (HT and MT)
Intermediate temperature design!
LD CU
HD CU
HD wisselaars
LD wisselaar
TD koeler

## Slide 14
Solution: 2-stage NH3 hybrid heat pump

## Slide 15
Solution: 2-stage NH3 heat “integrator”
LT 10/4°C
CTW

## Slide 16
Solution: 2-stage NH3 hybrid heat pump
Flexibility:
Modus 1: 100% chiller, max LT demand
Modus 2: full LT demand, partload HT demand  MT cond
Modus 3: LT and HT in balance
Modus 4: LT demand too low, heat input using MT evap (CHP)
Modus 5: LT demand too low, heat input using MT evap (condensation heat of the chillers)
Modus 6: LT demand too low, heat input in LT evap
Modus 7: only heat input using MT evap
Design of TD = temperature of intercooler = f(modi)
modus 1: TD = 33°C (COP chiller = 6,31)
modus 3: TD = 47°C (COP chilling/heating = 5,35)
modus 7: TD = 36°C (COP heating = 4,9)

## Slide 17: Solution: 2-stage NH3 hybrid heat pump
3 modi:
- Enkel koelen

## Slide 18: Solution: 2-stage NH3 hybrid heat pump
3 modi:
- Enkel oppompen restwarmte

## Slide 19: Solution: 2-stage NH3 hybrid heat pump
3 modi:
- Evenwicht koelen en verwarmen

## Slide 20
Main component selection
LP compression
2x SCV250M-L
1/47 °C
Qc = 4.2 MW (modus 3)
speed = 3050 rpm
Thermosiphon oil cooler
560 kW Siemens motor IE4, VSD
Notes: We compared to GEA screws en Bitzer screw units (4xOSKA95)
At the end client opted for mycom

## Slide 21
Main component selection
*Modus 1: chiller operation, speed is limited due to LT evap design

## Slide 22
Main component selection
HP compression
2x V750XHP NH3 heat pump
47/93 °C
Qh = 5.7 MW (modus 3)
Speed = 1500 rpm
630 kW ABB motor IE4, VSD
Notes: Comparison between gea and sabroe, the >90°C condensation temperature  GEA, now Sabroe is also able to reach these condensation temperatures

## Slide 23
Main component selection

## Slide 24
2-stage NH3 hybrid heat pump (modus 3)
COP global= 5.35
5.7 MW 70/90/110°C
CONDENSOR
DESUPERHEATER
LT EVAPORATOR
4.2 MW 10/4°C

## Slide 25
2-stage NH3 hybrid heat pump (modus 3)
COP global= 5.35
5.7 MW 70/90/110°C
CONDENSOR
DESUPERHEATER
LT EVAPORATOR
4.2 MW 10/4°C

## Slide 26
2-stage NH3 hybrid heat pump

## Slide 27
2-stage NH3 hybrid heat pump

## Slide 28
Return on technical experiences
Stability of hydraulics connections (hardware & software)
Extra attention to the oil return system due to the open system
Vibration of both the LP & HP compressors
Condensation of NH3 during operation, stillstand and the different modi
Temperature of the machineroom

## Slide 29
Results

## Slide 30
Results

## Slide 31
Next step: MVC

## Slide 32
Thank you for your attention!