## Slide 2: Water-Ammonia HTHP with liquid injected and refrigerant lubricated twin-screw compressor
Koelplatform - Masterclass, Tim van Craeynest, Kenny Couvreur, Robin Tassenoy, Xander van Heule, Michel De Pape, Steven Lecompte
Department of ElectroMechanical, Systems and Metal Engineering
  Sustainable Thermo-Fluid Energy Systems (STFES)

## Slide 3: Global Energy Use
Boehlé et al., Energy Efficiency 2025: Industry, 2025
Weiss et al., Tackling heat electrification to decarbonize industry, 2024
Notes: Let’s put the research into perspective. To do this we start from the global energy use.
Of the total energy use, 38% is used by industry.
66% of industries’ energy use is for process heating.
And still 80% of that process heating is supplied by burning fossil fuels.

## Slide 4: Current Situation
de Boer et al., Strengthening Industrial Heat Pump Innovation: Decarbonizing Industrial Heat, 2020
Zühlsdor et al., Project 68 - industrial high-temperature heat pumps. task 1–technologies. yearly report 2025, 2025
Arpagaus, High-temperature heat pumps: market overview, state of the art, and application potential, 2026
Notes: Energy use for process heating can be split up per temperature range:
11% below 100°C, 26%between 100°C and 200°C, 11% between 200°C and 500°C and the remaining part is above 500°C
HP cover everything up to about 100°C, most HTHPs can cover up to between 100°C and 200°C, for a higher temperature, mostly MVR is added.

## Slide 5: Heat Upgrading in Energy Intensive Industry
200°C
Max lift:
100°C
~100kWth
200°C
Max: 250°C
25bar
Single stage
170°C
100°C
120°C
Notes: Therefor the upheat project from the moonshot initiative were started up.
The goal was to achieve 200°C with a HTHP, reaching a maximum lift of 100°C.

## Slide 6: Refrigerant Selection
HFO
HFC
HCFC
Natural refrigerants
CFC
Low GWP
No ODP
No PFAS
hydrocarbons
CO2
Water(R718)
NH3 (R717)
Non-/low flammability
Subcritical (small temperature glides)
McLinden et al., (R)Evolution of Refrigerants, 2020
McLinden et al, New refrigerants and system configurations for vapor-compression refrigeration, 2020
Garavagno et al., Trifluoroacetic Acid: Toxicity, Sources, Sinks and Future Prospects,2024
Vieren et al., Selection of pure and binary working fluids for high-temperature heat pumps: A financial approach, 2024
Notes: Once the temperature range was fixed, the refrigerant had to be selected.
1 no ODP
2 low or no GWP
3 No PFAS
4 due to the relatively small temperature glide, the cycle is best to be subcritical
5 No/ low flammability is required
This leaves us with water

## Slide 7: Demonstrator Setup
Main refrigerant circuit
water
Notes: With the refrigerant selected, the demonstrator can be constructed.
Important is that all the parts are stainless steel to resist the ammonia.
The complete

## Slide 8: Water
High discharge temperature
Liquid/2-phase-injection
250°C
Notes: But using water as a refrigerant results in some challenges.
First of all the high discharge temperature
This will be solved by using liquid or 2-phase injection.
But the high normal boiling temperature of 100°C also provides us with some challenges.

## Slide 9: Water
High discharge temperature
Liquid/2-phase-injection
Notes: But using water as a refrigerant results in some challenges.
First of all the high discharge temperature
This will be solved by using liquid or 2-phase injection.
But the high normal boiling temperature of 100°C also provides us with some challenges.

## Slide 10: Water
normal boiling point 100°C
Sub-atmospheric pressures
High pressure ratios
Low volumetric heating capacity
Addition of ammonia
Vacuum pressure testing!
Notes: This leads to sub-atmospheric pressures, high pressure ratios and low volumetric capacities.
To mitigate these challenges, ammonia is added.

## Slide 11: Water And Ammonia
Chart: T(°C)
Notes: How does adding ammonia relief these issues:
The sub-atmospheric pressures can be increased by adding ammonia
Not only the pressure, but the density will increase as well, resulting in a higher volumetric heating capacity
Adding ammonia will also increase the condensing pressure, but the pressure ratio will be reduced.
An added benefit of adding ammonia is that the mixture becomes zeotropic which allows for a better exergetic efficiency by matching the glides.

## Slide 12: Water And Ammonia
↑
↑
↓
Sub-atmospheric pressures
High pressure ratios
Low volumetric heating capacity
↑
Vieren et al., Design of a high-temperature heat pump providing heat up to 200 °C, 2024
Notes: How does adding ammonia relief these issues:
The sub-atmospheric pressures can be increased by adding ammonia
Not only the pressure, but the density will increase as well, resulting in a higher volumetric heating capacity
Adding ammonia will also increase the condensing pressure, but the pressure ratio will be reduced.
An added benefit of adding ammonia is that the mixture becomes zeotropic which allows for a better exergetic efficiency by matching the glides.

## Slide 13: Temperature glide
T
s
250°C
Ammonia fraction condenses last
(and evaporates first)
Temperature glide
condensing

## Slide 14: Water And Optimal Ammonia Concentration
T
s
250°C
Optimal ammonia fraction
Sink
Pure water
200°C
170°C
86,5 mol % water
13,5 mol % ammonia
Smaller temperature difference between fluids:
Reduce exergy losses

## Slide 15: Demonstrator Setup
Stainless steel parts
(resistant to ammonia)
Main refrigerant circuit
Injection circuit
Lubrication circuit
High T: Oil degradation
Oil-free, hydrodynamic bearings
Challenge: Prevent evaporation
Notes: With the refrigerant selected, the demonstrator can be constructed.
Important is that all the parts are stainless steel to resist the ammonia.
The complete

## Slide 16: Main Refrigerant Circuit
Liquid injection
↑
Twin screw compressor (TSC)?
↓
liquid carryover tolerance ↑
Vieren et al., Design of a high-temperature heat pump providing heat up to 200 °C, 2024
Oil-free
Hydrodynamic bearings ✔
Twin screw compressor (TSC)!

## Slide 17: Heat Pump Setup

## Slide 18: Dimensions demonstrator
1320 mm
1880 mm
1520 mm
1677 mm
2002 mm
3119 mm
Front view

## Slide 19: Dimensions demonstrator
4720 mm
2850 mm
3194 mm
Top down view
Evaporator
Compressor
+motor
valves

## Slide 20: Demonstrator images
Spilling tank

## Slide 21: Planning
Short term | 2026 |  |  | 2027 |  |  |  |  |  |  |  | 
 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Commissioning lubrication circuit |  |  |  |  |  |  |  |  |  |  |  | 
Startup procedure |  |  |  |  |  |  |  |  |  |  |  | 
Lubrication circuit tests |  |  |  |  |  |  |  |  |  |  |  | 
Operation range test |  |  |  |  |  |  |  |  |  |  |  | 
… |  |  |  |  |  |  |  |  |  |  |  | 
Long term | 2028 |  |  |  |  |  |  |  |  | 2029 |  | 
 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3
Upheat-B2I project |  |  |  |  |  |  |  |  |  |  |  | 
Water
Water
Water
Water
+Ammonia
+Ammonia

## Slide 22: Conclusion
Water (R718)
p↓: ammonia (R717)
Tdischarge ↑: liquid / 2-phase injection
Twin-screw
↑
liquid carryover tolerance ↑
Loops
Main refrigerant
Liquid/2-phase injection
Lubrication circuit
Target
200°C supply
100°C lift
single stage

## Slide 23: Tim Van Craeynest Department of ElectroMechanical, Systems and Metal Engineering Sustainable Thermo-Fluid Energy Systems (STFES) E tim.vancraeynest@ugent.be Water-Ammonia HTHP with liquid injected and refrigerant lubricated twin-screw compressor
Universiteit Gent @ugent
@ugent Ghent University

## Slide 24: Heat Upgrading in Energy Intensive Industry
200°C
Max lift:
100°C
~100kWth
Notes: Therefor the upheat project from the moonshot initiative were started up.
The goal was to achieve 200°C with a HTHP, reaching a maximum lift of 100°C.

## Slide 25: HTHP Design Demonstrator
200°C
Max: 250°C
25bar
Single stage
170°C
100°C
120°C
Notes: This was translated into the following design:
170°C inlet temperature at the sink.
120°C inlet and 100°C outlet at the source
Maximum 250°C and 25bar mostly for material compliance.
And all of this in a single stage

## Slide 26: Bearing Lubrication Circuit
accommodates charge variations
provides temporary refrigerant supply during start‑up
Liquid receiver
Saturated Liquid
Liquid
Liquid
Potential cavitation
4-step channel pumps

## Slide 27: Bearing Lubrication Circuit
accommodates charge variations
provides temporary refrigerant supply during start‑up
Liquid receiver
Saturated Liquid
Liquid
Liquid
Potential cavitation
4-step channel pumps
Prevent evaporation when p↓
Subcooling with source fluid
Prevent evaporation↓
Increase backpressure

## Slide 28: Bearing Lubrication Circuit
Leakage to main flow in compressor
Refilling valve

## Slide 29: Water-Ammonia HTHP with liquid injected and refrigerant lubricated twin-screw compressor

## Slide 30: Optimal Ammonia Concentration
Boundary
conditions
PPTD = fixed
Condenser out = saturated (liquid receiver)
Sink temperatures = fixed
T
s
250°C
Sink
86,5 mol % water
13,5 mol % ammonia
Optimal ammonia concentration
Optimal discharge temperature
Vieren et al., Design of a high-temperature heat pump providing heat up to 200 °C, 2024
Vieren et el., Advancing Industrial High-Temperature Heat Pumps through Financial, Thermodynamic and Technological Evaluation, 2025
Notes: How was the optimal ammonia concentration decided
The boundery conditions are the following:
The PPTD is Fixed
The condenser outlet state is saturated (a little spoiler here but this is because there will be a liquid receiver after the condenser)
The sink temperatures are known
And the maximum temperature is 250°C
Furthermore, Vieren et al. found that the maximum allowable COP is found when the discharge temperature is at the limit. (trade-off more isothermal compression vs higher condensing pressures)
And lastly by adding ammonia the temperature glide will change. For small fractions of ammonia this result in an increased glide temperature difference when the ammonia fraction increases.

## Slide 31: Water And Optimal Ammonia concentration
T
s
250°C
Increased ammonia fraction
Sink
86,5 mol % water
13,5 mol % ammonia
Notes: Going to higher concentrations, the matching is again lost and the PP is now at the sink inlet.

## Slide 32: Bearing Lubrication Circuit
Leakage to main flow in compressor
Only open when compressor ON:
Cv = 0.1
Refilling valve

## Slide 33: Demonstrator images

## Slide 34: Demonstrator images